## KITCHEN
Country Cricket Club
JSCA International Stadium Complex, Dhurwa Ranchi-834004
BOQ FOR KITCHEN
Academy Building
1 | WORK TABLE WITH 2 U/S | 18" X 24"X 32" +4" | 1
2 | 2 BURNER GAS RANGE WITH 1 U/S | 42" X 24" X 32" + 4" | 1
3 | SINGLE SINK UNIT | 24" X 24" X 32" +4" | 1
4 | 2 BURNER GAS RANGE WITH 1 U/S | 42" X 24" X 32" + 4" | 1
5 | WORK TABLE WITH 2 U/S | 18" X 24" X 32" +4" | 1
6 | WORK TABLE WITH 2 U/S | 18" X 32" X 36" X 4" | 1
7 | SS TANDOOR -CHARCOAL | 32" X 32" X 36" | 1
8 | DOSA PLATE - GAS OPERATED | 48" X 24" X 34" | 1
9 | WORK TABLE WITH SINK | 48" X 24" X 34" | 1
10 | 2 DOOR U/C REFRIGERATOR+ 2 OHS | 60" X 24" X 34" | 1
10A | DOUBLE OVERHEAD SHELVES | 60" X 18" +12" | 1
11 | PICKUP COUNTER WITH 2 OHS | 60" X 24" X 34" | 1
11A | DOUBLE OVERHEAD SHELVES | 60" X 18" +12" | 1
12 | U/C REFRIGERATOR WITH 2 OHS | 60" X 24" X 34" | 1
12A | DOUBLE OVERHEAD SHELVES | 60" X 18" +12" | 1
13 | TILTING WET GRINDER | 7.5 LTR | 1
14 | PULVERIZER | 3 HP | 1
15 | 4 DOOR VERTICAL REFRIGERATOR | 48" X 24" X 84" | 1
20 | VEG TABLE RACK | 18" X 24" X 60" | 1
21 | 5 CONTAINER HOT BAIN MAIRE 1/1 X 150 MM DEEP 3 NOS +1/1 X 150 DEEP 2 NOS G N PAN | 72" X 26" X 34" | 1
22 | THALI /PIKAL / SALAD COUNTER | 24" X 26" X 34" | 2

## EXHAUST
Country Cricket Club
JSCA International Stadium Complex, Dhurwa Ranchi-834004
BOQ FOR Academy Building
EXHAUST SYSTEM
1 | EXHAUST HOOD WITH BAFFLE FILTTER - (FOR 2 BURNER GAS RANGE ) | 42" X 24" | 2
2 | EXHAUST HOOD WITH BAFFLE FILTTER - (FOR TANDOOR ) | 32" X 32" | 1
3 | EXHAUST HOOD WITH BAFFLE FILTTER - (FOR DOSA PLATE ) | 48" X 24" | 1
4 | EXHAUST FAN: PROVIDING & FIXING ON SITE 3 HP FAN DIRECT DRIVE CENTRIFUGAL - S.I.S.W FAN TO HAVE BACKWARD INCLINED BLADES IMPELLERS SHOULD BE STATICALLY AND DYNAMICALLY BALANCED . 960 RPM -MAKES OF HINDUSTAN OR EQUIVALENT. FAN MOTOR HAVE SQUIRREL CAGE , TO OPERATE ON 3 PHASE 50HZ AC SUPPLY WITH NECESSARY RAIN PROTECTIVE COVER FOR MOTOR WITH NECESSARY RAIN PROTECTIVE COVER FOR MOTOR WITH GALVANIZED SHEET. MOTOR SUITABLE TO RUN FOR 2 HOURS A DAY CONTINUOUSLY WITH EFFCIENCY OF 85% TO 90% | 900 Sq fit Approx. | 1
5 | M.S.STANDS FOR EXHAUST AIR FAN -SIZE TO BE COMPATABLE TO THE BLOWER FAN. STAND SHOULD BE PAINTED WITH 2 COAT OF ZINC CHROMATE PRIMER AND 2 COATS EPOXY PAINT. ENTIRE STAND TO BE WELL MADE - WITH ALL EXCESSIVE BURRS WELL GRIOUNDED & FINISHED & THEN SUITABLY GALVANISED |  | 1
6 | ANTI -VIBRATION PADS: PROVIDING AND FIXING HEAVY DUTY-DUNLOP MAKE ANTI VIBRATION PADS OF SUITABLE HEIGHT UNDER THE FAN -EACH SUITABLE TO TAKE LOAD OF 250 KG |  | 4
7 | DUCTING WORKS: DUCTING WORKS TO BE FABRICATED FROM 22 G.G.I.SHEET COMPLETE WITH SUPPORTS BRACKETS , FELT PACKING , ETC SHEETS TO BE OF JINDAL /SAIL MAKE ONLY -PREFERABLY JINDAL DUCTS TO BE OF 18G BUT WHERE NECESSARY ADEQUATE M.S.ANGLE FRAMEWORKS TO BE CLEANED AND PROPERLY GALVANISED MUST BE PROVIDED FOR LARGER DUCTS TO HOLD UP THE INNER SIDE FROM NOT CAVING IN DURING OPERATIONS. ALL DUCTING SHOULD BE OF FLANGE TYPE CONSTRUCTION -UNLESS SPECIFICALLY ASKED - TO BE OF SLIP TYPE CONSTRUCTION. ALL NUT BOLTS USED SHOULD BE OF ISI APPROVED -ZINC COATED TYPE. LOW DUCT VELOCITIES TO TAKE CARE OF NOISE. | 1200 SQ FIT Approx. | 1
8 | CANVAS CONNECTIONS ALL FAN CANVAS CONNECTION SHOULD BE OF THICK CANVASAND SHOULD HAVE DOUBLE CANVAS FLANGE - SO AS TO PREVENT RATS AND OTHER RODENTS EATING INTO IT ( WOULD BE PROVIDED WITH SS MESH ALL AROUND ) WIRE MESH OF T-304 STAINLESS STEEL QUALITY , WIRE DIAMETER 1.1938 MM, 4 X 4 WIRES PER 2.54 CM WITH OPENING |  | 1
PART-2 FRESH AIR SYSTEM
9 | TUBE AXIAL FAN 3 PH ,1 HP , 1440 RPM.CAPACITY OF FANS TO BE OF 5500 CFM EACH FOR 2 HP AT STATIC PRESSURE OF 1.5" WG .IMPELLER TO BE STATICALLY & DYNAMICALLY BALANCED- COMPLETE WITH MOUNTING ARRANGEMENT OF - GMS CRC SHEET. MOTOR MUST BE OF 1 HP MAKES OF BHARAT BIJLEE / CROMPTON / SIEMENS /WQUIVALENT. BODY OF FAN TO BE OF 3 MM THICK M.S.DULY RUSTPROOFED & PAINTED WITH EPOXY PAINT ON OUTSIDE MOTOR SUITABLE TO RUN FOR 2 HOURS A DAY CONTINUISLY WITH EFFICIENCY OF 85 % AT FULL LOAD. | 800 sq Fit Approx | 1
10 | FRESH AIR DUCTING WORKS: DUCTING WORKS TO BE FABRICATED FROM 20 G . G.I.SHEETS COMPLETE WITH SUPPORTS , BRACKETS , FELT PACKING , ETC SHEETS TO BE OF JINDAL/SAIL MAKE ONLY- PREFERABLY JINDAL. | 1000 SQ FIT approx. | 1
11 | FRESH AIR GRILL ALL DUCTING SHOULD BE OF FLANGE TYPE CONSTRUCTION . ALL NUT BOLTS USED SHOULD BE ISI APPROVED -ZINC COATED TYPE LOW DUCT VELOCITIES TO TAKE CARE OF NOISE |  | 6
12 | CANVAS COUNTER FLANGES ALL FAN CANVAS CONNECTIONS SHOULD BE OF THICK CANVAS AND SHOULD HAVE DOUBLE CANVAS FLANGE - SO AS TO PREVENT RATS AND OTHER RODENTS EATING INTO IT ( WOULD BE PROVIDED WITH SS MESH ALL AROUND ) WIRE MESH OF T-304 STAINLESS STEEL QUALITY , WIRE DIAMETER 1.1938 MM , 4X 4 WIRES PER 2.54 CM WITH OPENING OF 5.16 MM |  | 1

## CIVIL ELECTRIC
Country Cricket Club
JSCA International Stadium Complex, Dhurwa Ranchi-834004
MEP FOR Academy Building ( CIVIL , PLUMBING & ELECTRIC )
SR. NO. | PARTICULARS |  | Qty
CIVIL
4 | Providing and fixing 600 mm × 600 mm (2’ × 2’) ceramic/vitrified wall tiles of approved make and shade on prepared surface using polymer modified tile adhesive, including spacers, cutting, edge finishing, grouting with suitable grout, scaffolding, curing, and all materials, labour, tools, and wastage complete as per drawings and specifications. | SQ.FT | 1500
PAINTING
6 | Providing and applying walls to obtain smooth surface, followed by primer and three coats of Birla Opus Luster paint, including surface preparation, putty touch-up if required, materials, labour, scaffolding, curing, tools, and finishing complete as per manufacturer specifications and Engineer-in-charge instructions. | SQ.FT | 2000
PLUMBING
7 | Providing and installing a complete internal water supply and drainage system for the kitchen facility, comprising CPVC/PPR piping for cold and RO water distribution to all preparation, cooking, washing, storage, and utility areas; fixing angle valves, wall-mounted faucets, hot-cold mixers, and pre-rinse units at designated points; connecting all sinks and floor drains through UPVC piping to the main drain , carrying out testing, flushing, and commissioning of the entire plumbing network for all kitchen ( TOTAL 6 NOS FACUTS WITH ANGLE COCK ) |  | 1
ELECTRICAL
8 | As per the shared electrical layout, the scope includes supply, installation, wiring, testing and commissioning of complete electrical works comprising LED lighting fixtures, , 6/16 A socket outlets, 3-phase power points for kitchen equipment with isolators, distribution boards, main LT/MDB panel, earthing system, all associated cabling, conduits/cable trays, terminations, accessories and integration required for a fully functional installation. ( TOTAL 20 NOS SOCKETS 16 AMP /5 AMP & 4 NOS STARTER L &T & 10 NOS LED LIGHT OF 25 WATT ) |  | 1
DOOR
9 | FRD DOOR FOR FIRE EXIT | NOS | 2
GAS PIPE LINE
10 | GAS PIPELINE SYSTEM- Gas pipeline routing done using 1/2" TATA "C" Class seamless pipe with 3" heavy guage wall clamp .Individeal Control Valve with 5 Feet length Burner Pigtails.Akk necessary Fittings. Non Return Valve pressure Gauge, Pressure Regulator, Cylinder Pigtails, Cylinder Regulator connected to 3 cylinder Manifold and wall Clamp. ( With Gas Bank) | NOS | 1